# PRODUCT SPECIFICATION GUIDE

## MODEL: STATIC FIRE DAMPERS

# DIVISION 23 - Heating, Ventilation, and Air Conditioning (HVAC) 
(PREVIOUSLY DIVISION 15)

***************************************************************************************************************

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) Format.

The section must be carefully reviewed and edited by the Engineer to meet the requirements of the project and local building code.  Coordinate with other specification sections and the drawings.

Delete all "Specifier Notes" when editing this section.

## ***************************************************************************************************************

SECTION 233313 (Previously 15820)

STATIC FIRE DAMPERS

GENERAL

SECTION INCLUDES

Out of partition static fire dampers with curtain style blades meeting the requirements of the latest edition of UL Standard 555.

SUMMARY

Section 233100 – HVAC Ducts and Casings (Previously 15810).

REFERENCES

- AMCA 500-D – Laboratory Test Methods for Testing Dampers for Ratings.

- AMCA 511 - Certified Ratings Program for Air Control Devices.

- IBC – International Building Code.

- CSFM - California State Fire Marshall Listing for Fire Damper.

- MEA – City of New York, Department of Buildings, Material and Acceptance Division.

- NFPA 90A - Installation of Air Conditioning and Ventilating Systems.

- NFPA 101 – Life Safety Code.

- UL 555 - Standard for Safety; Fire Dampers.

SUBMITTALS

- Comply with requirements of Section 013300 - Submittal Procedures.

- Product Data:  Submit manufacturer's product data.

  - Include UL ratings, fire resistance, size limitations, and mounting orientation.

  - Indicate materials, construction, dimensions, and installation details.

  - Verify conformance to NFPA, UL, MEA, CSFM, and applicable building code.

  - Include a copy of UL approved installation instructions.

QUALITY ASSURANCE

Dampers shall be warranted against manufacturing defects for a period of 5 years.

Dampers shall be tested, rated and labeled in accordance with the latest UL-555 requirements.

Comply with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems," and with NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

Damper pressure drop ratings shall be based on tests and procedures performed in accordance with AMCA 500.

DELIVERY, STORAGE, AND HANDLING

Delivery:  Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer, material, and location of installation.

Storage:  Store materials in a dry area indoor and protected from damage and in accordance with manufacturer’s instructions.

Handling:  Handle and lift dampers by sleeve or frame only.  Do not lift damper by blades or jackshaft.  Protect materials and finishes during handling and installation to prevent damage.

PRODUCTS

MANUFACTURER

Pottorff, 5101 Blue Mound Road, Fort Worth, TX 76106.  Phone (817) 509-2300, www.pottorff.com.

OUT OF PARTITION STATIC FIRE DAMPERS

Model:  VFD-10-OP static curtain fire dampers.

Ratings:

Fire Rating: 1½ hours in accordance with UL-555.

*************************************************************************************************************

Specifier Notes: UL 555 provides for classification of fire dampers with fire resistance ratings of either 1 ½ or 3 hours.  NFPA 90A requires that HVAC penetrations through barriers with fire resistance ratings less than 3 hours be protected by 1 ½ hour rated dampers.  Penetrations through barriers with fire resistance ratings of 3 hours or more require 3 hour rated dampers.  NFPA 90A also requires that all fire damper locations and their hourly rating requirements be shown on the project plans.  Specifier, select from the following:

*************************************************************************************************************

Construction:

Frame:  Minimum 22 gauge (0.85 mm) roll formed, galvanized steel.

Blades:  Minimum 24 gauge (0.6 mm) roll formed, galvanized steel, curtain type.

Sleeve: Standard 14” long, 18 gauge (406 x 1.3), with ¾” flange, factory installed and wrapped with thermal blanket.

Release Temperature:

*************************************************************************************************************

Specifier Notes:  Building codes typically require the damper releasing temperature to comply with one of the following:

1. 	The operating temperature shall be approximately 50°F (10°C) above the normal temperature within the duct system, but not less than 160°F (71°C).

2. 	The operating temperature shall be not more than 286°F (141°C) where located in a smoke control system complying with Section 909.

Consult your local building code for further details and select one of the following.

*************************************************************************************************************

- 165 ºF (74 ºC).

- 212 ºF (100 ºC).

Mounting:  Vertical and/or Horizontal.

Duct Transition Connection: Type A – Blades and frame in the air stream, rectangular connection.

EXECUTION

EXAMINATION

Examine areas to receive dampers.  Notify the Engineer of conditions that would adversely affect installation or subsequent utilization of dampers.  Do not proceed with installation until unsatisfactory conditions are corrected

INSTALLATION

Install dampers at locations as indicated on the drawings and in accordance with manufacturer’s UL approved installation instructions.

Install dampers square and free from racking with the blades running horizontally.  DO NOT compress or stretch damper sleeve or frame into the duct or opening.

Contractor shall furnish and install duct access door adjacent to dampers for inspection and maintenance.  Where duct size permits, install minimum 12 inches x 12 inches (305 x 305 mm) duct access doors.

Handle dampers using the frame or sleeve.  Do not lift or move damper using blades or jackshaft.

END OF SECTION